TECHNICAL SERVICE REPORT

Water Analysis

| Customer: | Location: | Date: | PO#: |
| --- | --- | --- | --- |
| Chick-fil-A | # 2309 | 10/3/07 | 292825 |
| Address: |  | Tested By: |  |
| Shoppes @ North Village 5303 M. Belt Hwy St. Joseph, MO 64506 |  | AR |  |
| Phone: | Email: | Selecto Contact: |  |

| Recommendation: |  |
| --- | --- |

##### ANALYTICAL RESULTS

| Evaluation of: | Home Depot Water Sample | Target Water Sample | Recommended Max Levels |
| --- | --- | --- | --- |
| Chloride, ppm | 45 | 54 | 250 ppm |
| Sulfate, ppm | 122 | 118 | 250 ppm |
| Sodium, ppm | 25 | 20 | 250 ppm |
| Chloramine | Detected | Detected | .5 ppm |
| Chlorine, ppm | Detected | Detected | Detectable |
| Alkalinity, ppm | 170 | 170 | 150 ppm |
| Total Dissolved Solids, ppm | 300 | 310 | 500 ppm |
| Hardness, ppm | 200 | 225 | 100 ppm |
| pH | 7.7 | 7.9 | 6.5 – 8.5 ppm |
| Turbidity | 0.00 | 0.00 | .05 NTU |

The information supplied is believed to be accurate and is only indicative of the water tested.  The testing laboratory is not state certified.

3980 Lakefield Court    Suwanee, GA 30024    678.475.0799    800.635.4017

www.selectoinc.com

sales@selectoinc.com