TECHNICAL SERVICE REPORT

Water Analysis

| Customer: | Location: | Date: | PO#: |
| --- | --- | --- | --- |
| Chick-fil-A | # 2138 | 4/16/09 | 332743 |
| Address: |  | Tested By: |  |
| Renaissance Village FSU Durham, NC |  | AR |  |
| Phone: | Email: | Selecto Contact: |  |

| Recommendation: |  |
| --- | --- |

##### ANALYTICAL RESULTS

| Evaluation of: | #1 City Water | #2 Pump Head | #3 Filter Flush | #4 Water Spigot | Recommended Max Levels |
| --- | --- | --- | --- | --- | --- |
| Fluoride, ppm | 0.7 | 0.7 | 0.6 | 0.6 | 2 ppm |
| Chloride, ppm | 36 | 30 | 10 | 10 | 250 ppm |
| Nitrite, ppm | ND | ND | ND | ND | 1 ppm as N |
| Nitrate, ppm | 0.3 | 0.3 | 0.3 | 0.3 | 10 ppm as N |
| Sulfate, ppm | 61 | 60 | 59 | 59 | 250 ppm |
| Sodium, ppm | 38 | 35 | 24 | 23 | 250 ppm |
| Chloramine | Detected | Detected | ND | ND | .5 ppm |
| Chlorine, ppm | Detected | Detected | ND | ND | Detectable |
| Alkalinity, ppm | 16 | 15 | ND | ND | 150 ppm |
| Total Dissolved Solids, ppm | 180 | 170 | 115 | 115 | 500 ppm |
| Hardness, ppm | 32 | 32 | 26 | 24 | 100 ppm |
| pH | 7.2 | 7.4 | 6.5 | 6.5 | 6.5 – 8.5 ppm |
| Turbidity | 0.00 | 5.6 | 0.00 | 0.00 | .05 NTU |
| Iron, ppm | 0.03 | 0.64 | 0.00 | 0.00 | 0.3 ppm |

The information supplied is believed to be accurate and is only indicative of the water tested.  The testing laboratory is not state certified.

3980 Lakefield Court    Suwanee, GA 30024    678.475.0799    800.635.4017

www.selectoinc.com

sales@selectoinc.com