Type I Point of Use Recommended

TECHNICAL SERVICE REPORT

Water Analysis

| Customer: | Location: | Date: | PO#: |
| --- | --- | --- | --- |
| Chick-fil-A | # 2024 | 5/10/06 | 243537 |
| Address: |  | Tested By: |  |
| Wilson / Beltway 8 FSU 9525 North Sam Houston Parkway East Humble, TX 77396 |  | AR |  |
| Phone: | Email: | Selecto Contact: |  |

| Recommendation: | Type I Point of Use Recommended |
| --- | --- |

##### ANALYTICAL RESULTS

| Evaluation of: | Shell Mart Water Sample | Domino’s Water Sample | Recommended Max Levels |
| --- | --- | --- | --- |
| Fluoride, ppm | 0.2 | 0.2 | 2 ppm |
| Chloride, ppm | 60 | 62 | 250 ppm |
| Nitrite, ppm | ND | ND | 1 ppm as N |
| Nitrate, ppm | ND | ND | 10 ppm as N |
| Sulfate, ppm | 4.6 | 4.6 | 250 ppm |
| Sodium, ppm | 63 | 64 | 20 ppm |
| Ammonia as Chloramine | Must be tested on site | Must be tested on site | .5 ppm |
| Chlorine, ppm | Must be tested on site | Must be tested on site | Detectable |
| Alkalinity, ppm | 165 | 180 | 150 ppm |
| Total Dissolved Solids, ppm | 250 | 250 | 500 ppm |
| Hardness, ppm | 92 | 92 | 100 ppm |
| pH | 8.3 | 8.3 | 6.5 – 8.5 ppm |
| Turbidity | 0.60 | 0.70 | .05 NTU |

The information supplied is believed to be accurate and is only indicative of the water tested.  The testing laboratory is not state certified.

3980 Lakefield Court    Suwanee, GA 30024    678.475.0799    800.635.4017

www.selectoinc.com

sales@selectoinc.com